## Sheet1
Power Loss due to Cable Length - PowerPal Micro-hydro Generators
Power output | Voltage | Current | Cable diameter | Cable area | Loss | Cable length | Cable Length | Power loss | Avail. Power | Voltage loss | Avail. Voltage
W | V | A | mm | sq.mm | Ohms/km | m | Miles | W | W | V | V
650 | 260 | 2.5 | 1.5 | 1.7671 | 9.7 | 1300 | 0.80019 | 157.625 | 492.375 | 63.05 | 196.95
Insert data into the blue fields to observe the available power and voltage after power loss. Do not change other fields.
Note - Use for cable diameters 1.0, 1.1, 1.2, 1.3, 1.4, 1.5 and 2.0 only.
For 3kW system:
Power output | Voltage | Current | Cable diameter | Cable area | Loss | Cable length | Cable Length | Power loss | Avail. Power | Voltage loss | Avail. Voltage
W | V | A | mm | sq.mm | Ohms/km | m | Miles | W | W | V | V
3000 | 400 | 7.5 | 4.5 | 15.9043 | 0.6 | 1000 | 0.61553 | 67.5 | 2932.5 | 9 | 391
For 4kW system
Power output | Voltage | Current | Cable diameter | Cable area | Loss | Cable length | Cable Length | Power loss | Avail. Power | Voltage loss | Avail. Voltage
W | V | A | mm | sq.mm | Ohms/km | m | Miles | W | W | V | V
4000 | 400 | 10 | 4.5 | 15.9043 | 1.1 | 1000 | 0.61553 | 220 | 3780 | 22 | 378
Gauge | Diameter | Area
AWG | (mm) | sq. mm
1 | 7.35 | 42.4293
2 | 6.54 | 33.5928
3 | 5.83 | 26.6949
4 | 5.19 | 21.1556
5 | 4.62 | 16.7639
6 | 4.12 | 13.3317
7 | 3.67 | 10.5785
8 | 3.26 | 8.3469
9 | 2.91 | 6.6508
10 | 2.59 | 5.2685
11 | 2.31 | 4.191
12 | 2.05 | 3.3006
13 | 1.83 | 2.6302
14 | 1.63 | 2.0867
15 | 1.45 | 1.6513
16 | 1.29 | 1.307
17 | 1.15 | 1.0387
18 | 1.02 | 0.81713
19 | 0.912 | 0.65325
20 | 0.812 | 0.51785
21 | 0.723 | 0.41055
22 | 0.644 | 0.32573
23 | 0.573 | 0.25787
24 | 0.511 | 0.20508
25 | 0.455 | 0.1626
26 | 0.255 | 0.051071
27 | 0.143 | 0.016061
28 | 0.08 | 0.0050266
AWG= American Wire Gauge